Silicon Valley Leadership Group
Energy Efficient Data Center
Demonstration Project

October 2009

Maximizing Cooling Efficiency in a Concurrently Maintainable and Fault Tolerant Data Center

Abstract

This case study demonstrates RagingWire’s approach to improving efficiency of the chilled water and cooling system from end to end. The case study describes RagingWire’s approach to the ASHRAE standards and the air equation while maintaining a fault tolerant, concurrently maintainable data center. The energy conservation measures (ECM) have demonstrated a savings of 2,123,930 kWh/year for the current load, and an estimated additional 3,500,000 kWh/year on full build out. The ECMs implemented are:

	Blanking plates and strip curtains to isolate the hot aisle and prevent mixing and contamination

	Wireless sensors to monitor and dynamically control CRAC units and the environment

	Chiller upgrade to reduce chiller restart from 13 minutes to 3 minutes during utility transitions

	VFDs for CRAC units to dynamically control under‐floor static pressure and discharge air

temperature control

	Installation of chimneys on CRAC units to raise return temperature, improving capacity and

preventing mixing

	Controls and monitoring implementation to support concurrent maintainability and fault tolerance

Project Case

RagingWire Enterprise Solutions designs, builds and operates a 200,000ft2 data center with N+2 redundancy across all systems providing concurrent maintainability with fault tolerance for all systems. The data center is cooled by a central chilled water plant of six 900‐1200 ton chillers with two nominal 600 ton water side economizers providing chilled water to 154 thirty and forty ton CRAH units on a four foot raised floor. RagingWire conducted an end to end analysis of the cooling cycle which resulted in numerous focus areas. A key design criterion for any initiative was to ensure that the concurrent maintainability and fault tolerant design philosophy was maintained. As ASHRAE TC9.9 issued new standards (shown in Table 1) in 2008, RagingWire was already in the process of evaluating the set points on the data floor and central chilled water plant. Even within the ASHRAE set point of 25C, which was changed to 27C in 2008 (Table 1), the main drivers for RagingWire in a co‐location environment to establish an air delivery set point were:

	Actual equipment and manufacturers specifications, including legacy equipment

	Mixing, causing a temperature gradient in the cold aisle

	Utility transition events or chiller failure causing a supply water or air temperature transient

	The ability to monitor and measure the environment and respond dynamically

	Maintaining sufficient static pressure and CFM to the equipment being cooled from an air balance perspective

	Ensure thermodynamic capacity and a design factor to account for an unexpected loss of cooling
event

From a starting point of 25C (77F), which could easily be based on 27C, we subtracted to adjust for three main factors:

	Mixing was an average of 8F without isolation prior to the
implementation of the ECMs on the cold aisle side of the racks

	Expected thermodynamic transient due to a utility transfer to generator, or a chiller failure;
RagingWire chillers from utility loss to stabilization took 13 minutes, which is significantly
influenced by the controls on the chill water pumps and CRACs, and volume of the chilled water
loop

	Thermodynamic reservoir for an unexpected cooling event.

Project Outcome

The initial ECM was hot aisle isolation using blanking plates and strip curtains across the datacenter. This reduced the temperature gradient in the cold aisle to an average of 2 to 3F from the floor to the top of the rack. RagingWire still faces challenges to accommodate co‐location requirements in relation to this method.

RagingWire implemented a wide array wireless sensor suite from SynapSense to monitor both static environmental conditions and dynamically react to changes in existing customer environments, or during the new customer deployments. With the SynapSense wireless sensor suite, RagingWire has an improved ability to monitor static pressure under the data floor. In 2007 through sealing of the data floor, including PDUs, unnecessary holes and use of cold locks, RagingWire raised static pressure from .06” to .115” average across the data floor.

Monitoring and measurement of temperatures throughout the data center, RagingWire raised the supply water temperature from 50F to 55F, while maintaining a CRAC discharge temperature of 66F. This resulted in two main energy efficiency gains:

1:	Improved chiller efficiency, saving over 1 million kWh per year

2:	Increased ton‐hours from two waterside economizers resulting in an additional 1 million kWh saved as shown in Figure 1.

With an upgrade to the York chillers, the restart time was reduced from 13 min to 3 minutes with an eventual target of 2 to 2.5 minutes. The results of the quick start are shown in Figure 2 and tested in April and August of 2009 as shown in Figure 3. Reduced recovery times should allow further increases in chilled water supply temperature.

New CRAC VFDs dynamically control the static pressure to .07” at approximately 600CFM per perforated tile, from .115”. The savings is 4.65kW per CRAC unit, while also providing for better dynamic response to changes in data floor conditions and failure scenarios. The VFDs provide for better operational wear on the unit, startup and power factor correction. The enhanced monitoring provided for controls changes on the CRAC units from return air temperature controlled to discharge air temperature controlled.

With the SynapSense wireless sensors, monitoring is both static and dynamic to accommodate changes in the data center environment.

Under the 32 foot ceilings, RagingWire installed CRAC “chimneys” on the units throughout the data floor, raising the top of the CRACs from 6ft to 12ft, and raising the intake temperature of the CRAC by 5F.

Next Steps

Through the implementation of the changes noted above, RagingWire has saved over 2 million kWh with estimated savings of over an additional 3.5 million kWh on build out and full project completions. The plan for going forward is raising the chilled water temperature supply to 60F. This chill water set point would still provide a conservative 71F supply on the air side with estimated additional savings of over 2 million kWh per year.

Future challenges on cooling include:

	Equipment manufacturer standardization

	Education

–	With 71F and up to 95F in cold and hot aisles, respectively, new operations practices are
necessary, especially in co‐location with a mixed customer base.

–	Data center infrastructure teams must continue to work more closely with their IT counterparts to ensure efficiency gains are being made not only on the back of house, but from the data center outward.

	Refinement of equipment operating in the data center by manufacturers (chillers, water side economizing, air side economizing)

–	Dynamic response and controls

–	Optimized operations for a data center

–	Water use, carbon footprint concerns, industry regulation and efficiency maximization.

Figures and Tables

Table 1‐ASHRAE TC9.9 2004 and 2008 recommended environmental envelope conditions.

Figure 1 – Differences in ton‐hours of cooling for waterside economizing from a chilled water return temperature of 65F versus 60F.

Figure 2 – York YK Chiller Restart differences. Note: temperatures are recorded at the chiller, and not loop bulk temperature.; an additional two minutes were reduced off the production version compared to what is shown in the red curve for quickstart +0.

Figure 3 – Building kW showing four transition events during April 2009 chiller plant redundancy testing and data gathering.